[image: image2.png]Hytten

BIENE




Lianyungang Hytten Meter Co.,LTD.

LXSG-15~50mm
Wireless Electronical Water Meter 
[image: image1.jpg]



1、Features 
Only one parts can be moving┄turbine, reduce mechanical wear, increased service life;

Vacuum sealed LCD ensures the dial keep free from fog and frost, Keep the reading clear in a long term service; 

Greatly improve the measurement accuracy, improve the measuring range; 

Piecewise linear optimization of the error curve of the water meter, the measurement accuracy is higher; 
LCD digital direct reading, accurate display measurement information;

Prompt and accurate measurement of reverse flow; 

Has the instantaneous flow display function;

Modular design, easy installation and maintenance;

Automatic calculation of step water price;

Combined with the valve,can achieve the advance payment and remote control function;

Automatic storage of historical water data;

Automatically upload data on specify date;

Remote diagnostics running status;

Protection level:IP68. 

2、Standards Compliance

ISO 4064 Class C for horizontal Installation;

《Electronic remote-reading water meter》（CJ/T 224-2012）.

3、Working Conditions 

Water temperature：0.1℃~+50℃  

Storage temperature：-10℃~+60℃

Water pressure:≤1.6 MPa

4、Technical parameters 
working voltage ：DC 3.6V 

current  parameters： 

Quiescent current ≤6μA  

Dynamic current ≤9μA    

Communication current≤500μA  

Continuous working time：More than 6 years 

Technical parameters of receiving module 

■ Built in TI 16 bit MSP series low power MCU
■ Using Semtech's sx1276 spread spectrum chip
■ Communication distance：1.8Km  

■ Output power:+20dBm(Max.) 

■ Sensitivity:-147dBm

■ Power Supply:3.0V~3.6V  
■ Baud rate：9600bps 

■ Communication protocol：188W 

■ Communication frequency：868MHz or 433MHz,

 Channel spacing 0.5MHz 

■ Communication mode：UART 

5、MAIN TECHNICAL SPECIFICATIONS
	Type
	Size   


	CLASS
	Qs
	Qn 
	Qt
	Qmin  
	Minimum Reading
	Maximum  Reading

	
	
	
	m3/h
	m3

	LXSG-15
	½"
	C
	3.0
	1.5
	0.0225
	0.015
	0.001
	99,999

	LXSG-20
	¾"
	
	5
	2.5
	0.0375
	0.025
	0.001
	99,999

	LXSG-25
	1"
	
	7
	3.5
	0.0525
	0.035
	0.001
	99,999

	LXSG-32
	1¼"
	
	12
	6
	0.09
	0.06
	0.001
	99,999

	LXSG-40
	1½"
	
	20
	10
	0.15
	0.1
	0.001
	99,999

	LXSG-50
	2"
	
	30
	15
	0.225
	0.09
	0.001
	99,999


6、Maximum Permissible Error 

From Qmin inclusive up to but excluding Qp is ±5% .

From Qp inclusive up to and including Qs is ±2% .
DIMENSIONS 
	Type
	Size   


	          Length
	         Width
	             Height
	Connecting               Thread

	
	
	mm
	

	LXSG-15
	½"
	165
	102
	121
	G3/4

	LXSG-20
	¾"
	195
	102
	122
	G1

	LXSG-25
	1"
	225
	112
	135
	G1-1/4

	LXSG-32
	1¼"
	230
	112
	136
	G1-1/2

	LXSG-40
	1½"
	245
	130
	172
	G2

	LXSG-50
	2"
	300
	130
	175
	G2-1/2


8、Installation Requirement 
Installation environment does not affect electromagnetic waves;

The meter should be installed in horizontal position with the direction of the flow as in dicated by the arrow cast in the meter body with the register face upwards; 

Pipeline must be flushed before installation;

The meter should be constantly full of water during operation;

The installation environment should avoid explosed in the sunlight and flooding;
Master antenna should be installed in the open height;

Try to avoid the interference of external factors to communication.

According to the working condition of water supply facilities to determine the type of water meter、 measuring characteristic and the diameter, the expected flow should be adapted to the Qmin to Qn flow. Not only according to the pipe size and don’t give attention to permanent flow to choose water meter.

Water meters should be avoided under excessive stress caused by pipeline and pipe fittings.

The water meter should be installed to avoid exposure in the sunshine, freezing, pollution and flooding.The high cold area should avoid to be installed outdoors, If must be installed in outdoor water meter, should adopt sun block, antifreeze measure, The water meter should not be affected by frost crack.
Should be taken measures to prevent adverse hydraulic conditions (cavitating、surge、 water hammer) to prevent water meters from being damaged.

Due to not install strictly according to aboved mention, the damage of water meter and its accessories, The installer is responsible for all the damage.

9、The insruction of Order

The name/type/Diameter of the water meter should be marked on the order.

Includes two connected pipe & nuts and sealing gaskets for the  corresponding calibre in S/C 
10、Quality Commitment

The product's quality guarantee period is one year, any reasonable installation,correct use,but there  is the interior of damage or malfunction caused by manufacturing (with the exception of freezing), and under the condition of the guarantee seal integrity, the company responsible for repair and exchange.

11、Disclaimer

If the seal was damaged or incomplete or intentionally damaged, the company is not liable;And the company does not undertake other related responsibilities other than water meters (including but not limited to the liability of water metering disputes due to water meter failures or errors)

LIANYUNGANG HYTTEN METER CO.,LTD.

Address: NO.8 Hanguo Industrial Development Zone,Luoyang village,Dunshang Town,Ganyu District, Lianyungang City.  

Tel：0518-85907891         Fax：0518-85907892
Http：//www. hyttenmeter.com  E-mail：hytten@hyttenmeter.com

[image: image2.png]